## Sheet1
REGION | RN | REG_ENT_NAME | CUSTOMER | CN | MAIL_ADDRESS | MAIL_CITY | COUNTY | MAIL_STATE | ZIP_CD | STREET_ADDRESS | INV_NO | ACTV_CD | INV_START_DT | INV_END_DT | INV_STATUS_DT | INV_STATUS | NOTICE_TYPE | NOV_DT | TRACK_NUM | VIOL_STATUS | CAT_CD | RULE_CITATION | MEDIA_NAME | ALLEGATION_TXT | RESOL_DESC_TXT
REGION 11 - AUSTIN | RN102956448 | WOODCREEK WWTP | Aqua Utilities, Inc. | CN602787509 |  |  | HAYS |  |  | 2611 Farm to Market Rd 2325 | 906162 | WWCMPL | 2011-01-28 | 2011-02-03 | 2011-04-07 | DAPPROVED | NOV | 2011-04-06 | 428461 | RESOLVED | B | 26.121 | WATER | Failure to prevent the unauthorized discharge of wastewater from the collection system. | The permittee submitted documentation on 02/03/2011 showing that the discharges were addressed. The force-main at first site was repaired and the force-main at the second site was replaced with stronger pvc pipe. Documentation submitted was in the form of trip tickets from vacuum trucks used to pick up the wastewater and invoice for replacement of pipe.
REGION 11 - AUSTIN | RN106069511 | JESTER KING CRAFT BREWERY | Jester King Craft Brewery, LLC | CN603800202 |  |  | HAYS |  |  | 13187 Fitzhugh Rd, Austin, TX 78736 | 907356 | SWMSGPRC | 2011-03-22 | 2011-03-22 | 2011-05-17 | DAPPROVED | NOV | 2011-05-17 | 432991 | RESOLVED | B | 281.25(a)(4) | WATER | Entity failed to obtain the TPDES MSGP (TXR050000) for Industrial Storm Water Discharges. | Jester King Craft Brewery Submitted a No Exposure Certification (NEC) for the TPDES MSGP TXR050000 at the end of October 2011. A record search of the TCEQ database indicates that the entity had obtained MSGP authorization on or about November 04, 2011 (authorization TXRNEY477). The violation for failing to obtain MSGP authorization is resolved.
REGION 11 - AUSTIN | RN103930053 | HIGHPOINTE SUBDIVISION WWTF | Hays County Municipal Utility District 5 | CN602690679 |  |  | HAYS |  |  | 1361 Cool Spring Way, Austin, TX 78737 | 920568 | WWTLPCCIDS | 2011-05-13 | 2011-05-13 | 2011-06-14 | DAPPROVED | NOV | 2011-06-15 | 436976 | RESOLVED | C | 319.6 | WATER | Failure to properly perform QA analysis for chlorine | On May 12, 2011, the operator began analyzing duplicate samples to meet the QA requirement.
REGION 11 - AUSTIN | RN102187630 | HAYS COUNTY WATER CONTROL & IMPROVEMENT DISTRICT 1 | Hays County Water Control and Improvement District 1 | CN600688246 |  |  | HAYS |  |  | 12930 Nutty Brown Rd, Austin, TX 78737 | 936073 | WWCCIDSMIN | 2011-06-29 | 2011-06-29 | 2011-07-13 | DAPPROVED | NOV | 2011-07-15 | 439574 | RESOLVED | B | 26.121(d) | WATER | Failure to prevent an unauthorized discharge | The operator cycled pump #1 off and on. The pump started working and pumped down the wet well. The operator cleaned up the solids. The liquids soaked into the ground. The operator removed and cleaned pump #2 and returned it to service. A new starter was ordered for pump #3. The wet well was cleaned with a vactor truck. No evidence of the unauthorized discharge was observed during the inspection on June 29, 2011.
REGION 11 - AUSTIN | RN101703288 | CITY OF BUDA WWTP | Guadalupe-Blanco River Authority | CN601180565 |  |  | HAYS |  |  | 525 Garison Rd, Buda, TX 78610 | 956152 | WWCCIMDMAJ | 2011-09-14 | 2011-09-14 | 2011-10-03 | DAPPROVED | NOV | 2011-09-30 | 446889 | RESOLVED | C | 305.125(1) | WATER | Failure to meet effluent limit of 1 mg/L for chorine residual | The chlorine feed rate was adjusted. At 3:15 pm, chief operator, Ed Boettner, reported the chlorine residual was 1.5 mg/L.
REGION 11 - AUSTIN | RN102182680 | CITY OF KYLE WWTP | Aqua Operations, Inc. | CN602931685 | 941 NEW BRIDGE DR | KYLE | HAYS | TX | 78640 | 941 NEW BRIDGE DR , KYLE , TX 78640 | 987399 | WWCCIMDMAJ | 2012-02-08 | 2012-02-08 | 2012-02-29 | DAPPROVED | NOV | 2012-02-29 | 458600 | RESOLVED | B | 26.121(a)(3) | WATER | Failure to prevent unauthorized discharges | The unauthorized discharges were cleaned up and disinfected as appropriate. The line blockages were cleared. The City of Kyle has a program to replace or repair wastewater lines as needed. The City also has a program to jet clean lines, inspect manholes, and inspect wastewater lines with cameras, and to make repairs as necessary. The City has also replaced approximately 918 clean-outs to reduce I/I since August 2010.
REGION 11 - AUSTIN | RN100838648 | CITY OF SAN MARCOS WWTP | City of San Marcos | CN600521272 | 630 E HOPKINS ST | SAN MARCOS | HAYS | TX | 78666 | 630 E HOPKINS ST , SAN MARCOS , TX 78666 | 995353 | WWSSOMAJFC | 2012-01-25 | 2012-01-25 | 2012-03-23 | DAPPROVED | NOV | 2012-03-26 | 462235 | RESOLVED | C | 305.125(5) | WATER | Failure to ensure that the facility and all of its systems of collection, treatment, and disposal are properly operated and maintained. | On April 9, 2012, Mr. Tom Taggert, Director of Public Services, submitted documentation showing that repairs to the inverted siphon were completed on April 6, 2012. The compliance documentation included a description of other measures being taken to prevent future discharges from this location and photos of the repair were also included.
REGION 11 - AUSTIN | RN103897567 | HAYS COUNTY MUD WWTP | Hays County Municipal Utility District 4 | CN602690661 |  |  | HAYS |  |  | 147 Terrace Ct, Austin, TX 78737 | 1008987 | WWTLPCCIDS | 2012-05-31 | 2012-05-31 | 2012-06-18 | DAPPROVED | NOV | 2012-06-18 | 468379 | RESOLVED | B | 305.125(1) | WATER | Failure to meet effluent limit for BOD | It was determined that the effluent exceedance was caused by not maintaining adequate dissolved oxygen levels in the mixed liquor. The operator was re-trained on process control and interpretation of lab data. Corrections were made, and the April 2012 BOD daily average was 5 mg/L.
REGION 11 - AUSTIN | RN102314218 | RAILYARD PLANT | Aus-Tex Parts & Services, Ltd. | CN601121122 |  |  | HAYS |  |  | 187 Depot Dr, Kyle, TX 78640 | 1015476 | WWCCIMDMIN | 2012-06-28 | 2012-06-28 | 2012-08-09 | DAPPROVED | NOV | 2012-08-10 | 470911 | RESOLVED | B | 210.4(a)(4) | WATER | Failure to obtain authorization to use reclaim water | Adequate compliance documentation was received on June 28 and July 27, 2012, to resolve the violation. On June 28, 2012, Mr. Morgan stated that "I have spoken with the contractor and they have agreed to remove their pumps and hoses. If any reuse is needed in the future we will work together to make sure the necessary paperwork is submitted to TCEQ and the proper permit is obtained. I will send you pics of the area in reference." A photograph was provided on July 27, 2012.
REGION 11 - AUSTIN | RN101513729 | GOFORTH WWTP | Aqua Utilities, Inc. | CN602787509 | 5271 GOFORTH RD | KYLE | HAYS | TX | 78640 | 5271 GOFORTH RD , KYLE , TX 78640 | 1042222 | WWCCIMDMIN | 2012-10-25 | 2012-10-25 | 2012-12-20 | DAPPROVED | NOV | 2012-12-21 | 486338 | RESOLVED | B | 305.125(1) | WATER | Exceeded 2-hour peak flow limit of 103 GPM during the weeks of 1/23/2012 and 2/26/2012 | Adequate compliance documentation was received on November 5 and December 11, 2012, to resolve the violation. Heavy rainfall of over 6 inches could have caused the flow exceedance on January 23, 2012. The ultrasonic flow meter was also found to be out of alignment on February 28, 2012, by Fluid Meter Services (FMS). FMS re-aligned the meter and certified the meter's accuracy on February 28, 2012. Mr. Bautista and Mr. Robinson will be monitoring the flow charts during days where high rainfall occurs, and will report any exceedances as necessary (on DMRs or via Noncompliance Notification if over 40%).
REGION 11 - AUSTIN | RN102597846 | BUDA PLANT | Texas Lehigh Cement Company LP | CN600127666 | 701 CEMENT PLANT RD | BUDA | HAYS | TX | 78610 | 701 CEMENT PLANT RD , BUDA , TX 78610 | 1073155 | WWTLPCCIDS | 2013-03-13 | 2013-03-13 | 2013-05-08 | DAPPROVED | NOV | 2013-05-09 | 500846 | RESOLVED | C | 305.125(1) | WATER | Failed to operate and maintain the facility a minimum of 5 days per week by a licensed operator. | The documentation submitted on 06/10/2013 was sufficient to resolve the violation. The daily logs now being kept by the permittee showed the plant is being checked by a properly licensed operator 5 days per week.
REGION 11 - AUSTIN | RN101677326 | HELDENFELS ENTERPRISES | Heldenfels Enterprises, Inc. | CN600836340 | 5700 S IH 35 | SAN MARCOS | HAYS | TX | 78666 | 5700 S IH 35 , SAN MARCOS , TX 78666 | 1123098 | WWCCIDSMIN | 2013-10-02 | 2013-10-02 | 2013-12-05 | DAPPROVED | NOV | 2013-10-11 | 521045 | RESOLVED | B | 26.121 | WATER | Failed to maintain compliance with the permitted effluent limits. Specifically, the grab sample collected during the investigation was not compliant with the single grab limit of 65 mg/L for Total Suspended Solids (TSS). The result of the TSS analysis was 160 mg/L. | On February 6, 2014, documentation was submitted to the TCEQ Austin Region Office which included a narrative description, photographic documentation, and sample results indicating that two consecutive compliant samples were obtained at all permitted outfalls. Structural modifications were made to the existing Best Management Practices (BMPs) leading to Outfall 003 in order to increase filtration of sediment.
REGION 11 - AUSTIN | RN104000658 | REUNION RANCH WASTEWATER PLANT A | Reunion Ranch WCID | CN603086588 | 100 JAYNE CV | AUSTIN | HAYS | TX | 78737 | 100 JAYNE CV , AUSTIN , TX 78737 | 1193464 | WWTLPCCIDS | 2014-09-04 | 2014-09-04 | 2014-10-29 | DAPPROVED | NOV | 2014-10-30 | 552084 | RESOLVED | C | 222.121(g)(1) | WATER | Failed to provide telemetry or SCADA with battery back-up to notify an operator of a malfunction at anytime. | Adequate compliance documentation was received on September 18, 2014, to resolve this issue as an area of concern.
REGION 11 - AUSTIN | RN103896148 | A E WOOD STATE FISH HATCHERY | Texas Parks And Wildlife Department | CN600134852 | 507 STAPLES RD | SAN MARCOS | HAYS | TX | 78666 | 507 STAPLES RD , SAN MARCOS , TX 78666 | 1221970 | ER ONSITE | 2014-12-22 | 2014-12-22 | 2015-01-30 | DAPPROVED | NOV | 2015-01-30 | 559472 | RESOLVED | B | 26.121 | WATER | Failure to prevent an unauthorized discharge of pollutants to the San Marcos River. Specifically, on December 15, 2014, the contents of a storm water detention pond were pumped and discharged to the river. The pipe was placed at the bottom of the pond allowing silt accumulations to enter. Proper Best Management Practices (BMPs) were not utilized to prevent the discharge of pollutants to water in the state. | TPWD took appropriate actions to resolve the incident including reporting the discharge, ceasing the discharge, and implementing structural and non-structural controls to prevent reoccurrence in the future.
REGION 11 - AUSTIN | RN101610350 | BLUE HOLE WWTF | City of Wimberley | CN603592239 |  |  | HAYS |  |  | 333 Blue Hole Ln, Wimberley, TX 78676 | 1223197 | WWTLPCCIDS | 2015-01-29 | 2015-01-29 | 2015-03-04 | DAPPROVED | NOV | 2015-03-05 | 563117 | RESOLVED | C | 305.125(1) | WATER | Failed to prevent ponding of effluent on the irrigation field | Adequate compliance documentation was received on February 4, 2015, to resolve this violation. On February 3, 2015, the pipe was repaired and the area was backfilled.
REGION 11 - AUSTIN | RN104005434 | CITY OF DRIPPING SPRINGS | City of Dripping Springs | CN602491284 |  |  | HAYS |  |  | 23127 Ranch to Market Rd 150, Driftwood, TX 78619 | 1289946 | WWCMPL | 2015-12-22 | 2015-12-22 | 2016-02-12 | DAPPROVED | NOV | 2016-02-10 | 594724 | RESOLVED | B | 305.125(1) | WATER | Failed to properly operate and maintain the facility. On December 16, 2015, a solenoid valve in the drip irrigation field failed to properly operate in zone 40 causing the saturation of zones 40 and 41. Treated effluent discharged off-site, south of the fields. The permitee reported that the total amount of treated effluent sent to these fields would have been 7,500 gallons and the estimated volume of the unauthorized discharge was approximately 3,750 gallons. | The permittee was notified of the discharge on December 16, 2015 and ceased the discharge. Zones 40 and 41 were turned off and were removed from the cycle until the system could be repaired. The discharge was reported via telephone to the TCEQ Austin Region within 24 hours and a written non-compliance notification was submitted within five days.
REGION 11 - AUSTIN | RN104789094 | MANDOLA ESTATE WINERY | Duchman, Ltd. | CN602936304 | 13308 FM 150 W | DRIFTWOOD | HAYS | TX | 78619 | 13308 FM 150 W , DRIFTWOOD , TX 78619 | 1376222 | WWTLPCCIDS | 2016-10-19 | 2016-10-19 | 2016-12-14 | DAPPROVED | NOV | 2016-12-14 | 625841 | RESOLVED | B | 305.125(1) | WATER | Failure to document leaks in the evaporation pond and remove the pond from service until it is repaired or replaced. Specifically, water was observed in the leak detection system and notations on monthly log sheets indicated that the system was dry. | On July 17, 2017 TCEQ Water Quality Assessment Team received documentation indicating violation resolution.
REGION 11 - AUSTIN | RN103898094 | A&M HEEP WWTP | Sunfield Municipal Utility District No. 4 | CN603116211 |  |  | HAYS |  |  | 1305 FM2001, Buda, TX 78610 | 1420964 | WWCCIMDMIN | 2017-06-01 | 2017-06-08 | 2017-08-07 | DAPPROVED | NOV | 2017-06-01 | 650024 | RESOLVED | C | 305.125(1) | WATER | Failed to properly operate and maintain the Facility and all of its systems of collection, treatment, and disposal. | During the June 8, 2017 investigation date, it was documented that the rubber skirt on the skimmer arm for the clarifier at Wastewater Treatment Train No. 1 had been replaced. Additionally, it was documented that adjustments had been made at the clarifier for Wastewater Treatment Train No. 2 to ensure that both rubber skirt sections were in contact with the water's surface.
REGION 11 - AUSTIN | RN101608255 | SALT LICK WWTP | "Driftwood Equities, Ltd." | CN600861660 |  |  | HAYS |  |  | 18300 RM 1826, Driftwood, TX 78619 | 1314065 | WWTLPCCIDS | 2017-05-02 | 2017-05-02 | 2017-06-30 | DAPPROVED | NOV | 2017-06-30 | 646570 | RESOLVED | B | 319.9(d) | WATER | Failed to assure the quality of all measurements through the use of blanks, standards, duplicates, and spikes. | On May 22, 2017, documentation was received reflecting that the operator began conducting the required QA/QC for the chlorine meter on May 5, 2017. On June 9, 2017, documentation was received reflecting that the operator began conducting the required QA/QC for the pH meter on May 25, 2017. Therefore, this deficiency is considered to be resolved as of June 9, 2017.
REGION 11 - AUSTIN | RN110448248 | DRIPPING SPRINGS PLANT 22 | Lauren Concrete, Inc. | CN605061001 | 4901 W HIGHWAY 290 | DRIPPING SPRINGS | HAYS | TX | 78620 | 4901 W HIGHWAY 290 , DRIPPING SPRINGS , TX 78620 | 1554087 | AIRCOMPL | 2019-03-27 | 2019-04-01 | 2019-04-17 | DAPPROVED | NOV | 2019-04-17 | 710327 | RESOLVED | C | 382.085(b) | WATER | Failure to notify the Austin Region Office of start of construction, no later than 15 working days after occurrence of the event. | On April 1, 2019, Lauren notified the TCEQ Austin Region Office that on March 1, 2019, construction had begun.
REGION 11 - AUSTIN | RN109475210 | INGRAM READY MIX PLANT | Ingram Readymix No. 13, L.L.C. | CN604019901 | 4785 TRANSPORTATION WAY | SAN MARCOS | HAYS | TX | 78666 | 4785 TRANSPORTATION WAY , SAN MARCOS , TX 78666 | 1577021 | WWCMPL | 2019-05-30 | 2019-05-30 | 2019-07-24 | DAPPROVED | NOV | 2019-07-25 | 719194 | RESOLVED | B | 26.040(e) | WATER | Failure to obtain authorization to discharge wastewater and stormwater from industrial activity associated with concrete producttion plant under TPDES Permit No. TXG110000. | On June 21, 2019, Ingram Ready Mix Plant acquired authorization from the TCEQ to operate a concrete production plant under Texas Pollution Discharge Elimination System General Permit no. TXG110000, via permit identification no. TXG112501.
REGION 11 - AUSTIN | RN105095905 | FIVE STAR CONCRETE | Five Star Concrete, Inc. | CN602684672 | 2 GRIST MILL RD | UHLAND | HAYS | TX | 78640 | 2 GRIST MILL RD , UHLAND , TX 78640 | 1618174 | WWCCIGNPER | 2020-01-13 | 2020-01-13 | 2020-02-04 | DAPPROVED | NOV | 2020-02-05 | 740256 | RESOLVED | B | 319.4 | WATER | During the January 8, 2020 compliance investigation, the responsible party did not provide whole effluent toxicity testing results after a initial discharge that occurred during 2019. | The compliance documentation received on May 4, 2020 resolves the violation.
REGION 11 - AUSTIN | RN102768231 | DRIPPING SPRINGS APARTMENTS | Dripping Springs Apartments, L.P. | CN601407265 |  |  | HAYS |  |  | 289 Springs Ln, Dripping Springs, TX 78620 | 1652772 | WWTLPCCIDS | 2020-05-26 | 2020-06-30 | 2020-08-21 | DAPPROVED | NOV | 2020-08-24 | 756825 | ACTIVE | B | 305.125(1) | WATER | Failed to initiate engineering and financial planning for expansion and/or upgrading the domestic wastewater treatment and/or collection facilities whenever flow measurements reach 75% of the permitted daily average or annual average flow for 3 consecutive months.
REGION 11 - AUSTIN | RN104526801 | HEADWATERS WATER RECLAMATION PLANT | WFC HEADWATERS OWNER VII, L.P. | CN604591925 |  |  | HAYS |  |  | 250 Sage Thrasher Cir, Dripping Springs, TX 78620 | 1678781 | WWCMPL | 2020-09-21 | 2020-09-21 | 2020-10-15 | DAPPROVED | NOV | 2020-10-16 | 760761 | RESOLVED | C | 26.039 | WATER | Failed to provide notification of any noncompliance which may endanger human health or safety, or the environment. | Compliance documentation received on October 1, 2020 was sufficient to resolve the violation, see Att. C for more information.
REGION 11 - AUSTIN | RN103930129 | CASTLETOP CAPITAL HAYS ABC WWTP | North Hays County MUD 1 | CN602563561 |  |  | HAYS |  |  | 225 Shadow Creek Blvd, Buda, TX 78610 | 1336886 | WWCCIMDMIN | 2021-02-10 | 2021-02-10 | 2021-03-10 | DAPPROVED | NOV | 2021-03-10 | 770573 | RESOLVED | B | 305.125(1) | WATER | Failed to prevent unauhtoirzed discharges. | All unauthorized discharges were reported to the TCEQ. The affected areas were cleaned up and disinfected.